## drive motors
CHP DRIVE MOTOR DETAILS
SL | LOCATION |  | HT/LT | KW | MAKE | RPM | FRAME | SL | DE | NDE
1 | AF 2 | 0 | LT | 37 | KIR | 1470 | LD2255MK | HA152-323 | 6313 | 6313
2 | CONV C1 | 18 | LT | 37 | BB | 1470 | 225 | M0306651 | 6213C3 | 6213C3
3 | AF 3 | 17 | LT | 55 | SIE | 1475 | 250M | 448118 | 6215C3 | 6215C3
4 | AF 1 | 0 | LT | 55 | ABB | 1480 | 225 | M0306754 | NA | NA
5 | PF 5 | 0 | LT | 75 | BB | 1480 | 280M | M0303243 | 6317C3 | 6316C3
6 | PF 6 | 0 | LT | 75 | BB | 1480 | 280M | M0303242 | 6317C3 | 6316C3
7 | PF 1 | 0 | LT | 90 | KIR | 1482 | LD280M | 28909115-3 | N318 | 6314
8 | PF 2 | 0 | LT | 90 | CG | 1485 | 280M | 835665-8701 | NA | NA
9 | PF 3 | 0 | LT | 90 | CG | 1480 | E280M | AEV10494 | 6318 | 6318
10 | PF 4 | 0 | LT | 90 | CG | 1480 | E280M | NA | 6318 | 6318
11 | CONV 3.1 | 8 | LT | 90 | HYN | 1447 | 315M | 89MSTH022 | 6318 | 6315
12 | CONV 3.2 | 9 | LT | 90 | HYN | 1447 | 315M | 89MSTH020 | 6318 | 6315
13 | CONV 4.1 | 10 | LT | 90 | HYN | 1447 | 315M | 89MSTH023 | 6318 | 6318
14 | CONV 4.2 | 11 | LT | 90 | HYN | 1500 | 350M | 89MSTH02X | 6318 | 6315
15 | CONV C4 | 22 | LT | 90 | BB | 1480 | D355L | M0307703 | 6317C3 | 6316C3
16 | CONV C9 | 0 | LT | 110 | KIR | 1471 | SC315S | 20901001-01 | NU310C3 | 6319C3
17 | CONV 1.1-P | 2 | HT | 132 | HYN | 1485 | 400 | NA | NU317 | 6317
18 | CONV 1.1-S | 3 | HT | 132 | HYN | 1480 | 400 | 89MSTH018 | NU317 | 6317
19 | CONV 1.2-P | 4 | HT | 132 | HYN | 1480 | 400 | 89MSTH017 | NU317 | 6317
20 | CONV 1.2-S | 5 | HT | 132 | HYN | 1480 | 400 | 89MSTH016 | NU318 | 6318
21 | CONV 2.1 | 6 | HT | 150 | CG | 1477 | 355L | 18900771 | NU221 | 6321C3
22 | CONV C3 | 21 | HT | 150 | CG | 1477 | D355L | 2003211-1 | NU221C3 | 6321C3
23 | CONV C7-P | 0 | HT | 150 | CG | 1477 | D355L | 2003211-3 | NU221C3 | 6321C3
24 | CONV C2-S | 20 | HT | 200 | CG | 1477 | D355L | 2003210/1 | NU221C3 | 6321C3
25 | CONV C5 | 23 | HT | 200 | CG | 1477 | D355L | 20032104 | NU221C3 | 6321C3
26 | CONV C7-S | 25 | HT | 200 | CG | 1477 | D355L | 2003210-1 | NU221C3 | 6321C3
27 | CONV C6 | 24
28 | CONV 2.2 | 7 | HT | 225 | KIR | 1480 | 425 | 3910103-1 | NA | NA
29 | CONV 5.1-P | 12 | HT | 250 | HYN | 1500 | 475M | 89MSTH010 | NV320 | 6320
30 | CONV 5.1-S | 13 | HT | 250 | HYN | 1500 | 475M | 89MSTH013 | NV320 | 6320
31 | CONV 5.2-P | 14 | HT | 250 | HYN | 1500 | 475M | 89MSTH012 | NV320 | 6320
32 | CONV 5.2-S | 15 | HT | 250 | HYN | 1500 | 475M | 89MSTH011 | NV320 | 6320
33 | CONV C2-P | 19 | HT | 250 | KIR | 1480 | D355L | 3080909-02 | 6322C3 | NU321C3
34 | CONV C8-S | 30 | HT | 250 | KIR | 1481 | SCX355F | 3080909-01 | 6322C3 | NU321C3
35 | CONV C8-P | 29 | HT | 250 | GEC | 1484 | 355 | 186062-1 | N321 | 6321
36 | CONV C10 | 31 | HT | 355 | KIR | 1490 | SCX400F | 3080816-02 | NU324C3 | 6322C3
37 | CONV C11 | 32 | HT | 355 | KIR | 1490 | SCX400F | 3080816-01 | NU324C3 | 6322C3
38 | GC 1 | 1 | HT | 400 | ABB | 992 | SCX-450-F | 4540507 | 6324C3 | 6324C3
39 | GC 2 | 0 | HT | 400 | ABB | 992 | SCX-450-F | 4540506 | 6324C3 | 6324C3
40 | GC 3 | 16 | HT | 480 | CG | 593 | TPR560E | 2002043/02 | NU230C3

## Sheet1
CHP DRIVE MOTORS
SL | LOCATION | HT/LT | KW | MAKE | RPM | FRAME | SL | DE | NDE
1 | GC 1 | HT | 400 | ABB | 992 | SCX-450-F | 4540507 | 6324C3 | 6324C3
2 | GC 2 | HT | 400 | ABB | 992 | SCX-450-F | 4540506 | 6324C3 | 6324C3
3 | GC 3 | HT | 480 | CG | 593 | TPR560E | 2002043-02 | NU230C3
4 | AF 1 | LT | 55 | BB | 1480 | 225 | M0306754 | NA | NA
5 | AF 2 | LT | 37 | KIR | 1470 | LD2255MK | HA152-323 | 6313 | 6313
6 | AF 3 | LT | 55 | SIE | 1475 | 250M | 448118 | 6215C3 | 6215C3
7 | PF 1 | LT | 90 | KIR | 1482 | LD280M | 28909115-03 | N318 | 6314
8 | PF 2 | LT | 90 | CG | 1485 | 280M | 835665-8701 | NA | NA
9 | PF 3 | LT | 90 | CG | 1480 | E280M | AEV10494 | 6318 | 6318
10 | PF 4 | LT | 90 | CG | 1480 | E280M | NA | 6318 | 6318
11 | PF 5 | LT | 75 | BB | 1480 | 280M | M0303243 | 6317C3 | 6316C3
12 | PF 6 | LT | 75 | BB | 1480 | 280M | M0303242 | 6317C3 | 6316C3
13 | CONV 1.1-P | HT | 132 | HYN | 1485 | 400 | NA | NU317 | 6317
14 | CONV 1.1-S | HT | 132 | HYN | 1480 | 400 | 89MSTH018 | NU317 | 6317
15 | CONV 1.2-P | HT | 132 | HYN | 1480 | 400 | 89MSTH017 | NU317 | 6317
16 | CONV 1.2-S | HT | 132 | HYN | 1480 | 400 | 89MSTH016 | NU318 | 6318
17 | CONV 2.1 | HT | 150 | CG | 1477 | 355L | 18900771 | NU221 | 6321C3
18 | CONV 2.2 | HT | 225 | KIR | 1480 | 425 | 3910103-1 | NA | NA
19 | CONV 3.1 | LT | 90 | HYN | 1447 | 315M | 89MSTH022 | 6318 | 6315
20 | CONV 3.2 | LT | 90 | HYN | 1447 | 315M | 89MSTH020 | 6318 | 6315
21 | CONV 4.1 | LT | 90 | HYN | 1447 | 315M | 89MSTH023 | 6318 | 6318
22 | CONV 4.2 | LT | 90 | HYN | 1500 | 350M | 89MSTH02X | 6318 | 6315
23 | CONV 5.1-P | HT | 250 | HYN | 1500 | 475M | 89MSTH010 | NV320 | 6320
24 | CONV 5.1-S | HT | 250 | HYN | 1500 | 475M | 89MSTH013 | NV320 | 6320
25 | CONV 5.2-P | HT | 250 | HYN | 1500 | 475M | 89MSTH012 | NV320 | 6320
26 | CONV 5.2-S | HT | 250 | HYN | 1500 | 475M | 89MSTH011 | NV320 | 6320
27 | CONV C1 | LT | 37 | BB | 1470 | 225 | M0306651 | 6213C3 | 6213C3
28 | CONV C2-P | HT | 250 | KIR | 1480 | D355L | 3080909-02 | 6322C3 | NU321C3
29 | CONV C2-S | HT | 200 | CG | 1477 | D355L | 2003210-1 | NU221C3 | 6321C3
30 | CONV C3 | HT | 150 | CG | 1477 | D355L | 2003211-1 | NU221C3 | 6321C3
31 | CONV C4 | LT | 90 | BB | 1480 | D355L | M0307703 | 6317C3 | 6316C3
32 | CONV C5 | HT | 200 | CG | 1477 | D355L | 2003210/4 | NU221C3 | 6321C3
33 | CONV C6
34 | CONV C7-P | HT | 150 | CG | 1477 | D355L | 3170417-1 | NU221C3 | 6321C3
35 | CONV C7-S | HT | 200 | CG | 1477 | D355L | 2003240-2 | NU221C3 | 6321C3
36 | CONV C8-P | HT | 250 | GEC | 1484 | 355 | 186062-1 | N321 | 6321
37 | CONV C8-S | HT | 250 | KIR | 1481 | SCX355F | 3080909-01 | 6322C3 | NU321C3
38 | CONV C9 | LT | 110 | KIR | 1471 | SC315S | 20901001-01 | NU310C3 | 6319C3
39 | CONV C10 | HT | 355 | KIR | 1490 | SCX400F | 3080816-02 | NU324C3 | 6322C3
40 | CONV C11 | HT | 355 | KIR | 1490 | SCX400F | 3080816-01 | NU324C3 | 6322C3

## non drive motors
NON DRIVE MOTORS
SL | LOCATION | HT/LT | RPM | KW | FRAME
1 | lubrication pump 1 | LT | 1460 | 7.5 | 132 M
2 | lubrication pump 2 | LT | 1460 | 7.5 | 132M
3 | lubrication pump phase II | LT | 1460 | 7.5 | 132 M
4 | tripper 1 | LT | 1460 | 7.5 | 132 M
5 | tripper 2 | LT | 1460 | 7.5 | 132M
6 | tripper phase II | LT | 1460 | 7.5 | 132 M
7 | DE system 1 |  | 1447 | 37 | 225 M
8 | DE system 2 |  | 1447 | 37 | 225 M
9 | DE system phase II |  | 1447 | 37 | 225 M
10 | appron feeder 1 |  | 1447 | 37 | 225 M
11 | appron feeder 2 |  | 1447 | 37 | 225 M
12 | appron feeder phase II |  | 1447 | 37 | 225 M
13 | conveyor c1 |  | 1447 | 37 | 225 M
14 | supply air fan |  | 1447 | 37 | 225 M
15 | sump pump no 1 (vertical) |  | 1460 | 15
16 | sump pump no 2 (vertical) |  | 1460 | 15
17 | sump pump phase II (vertical) |  | 1460 | 15
18 | ventilation fan phase II |  | 960 | 15
19 | ventilation fan 1 |  | 960 | 22
20 | ventilation fan 2 |  | 960 | 22
21 | cooling fan |  | 1460 | 0.37
22 | traveling motor for plough feeder |  | 1460 | 1.2
23 | heat exchanger |  | 2800 | 11

## CWS
CHP motors at CWS
SL | RATING | MAKE | SL | USE | SENT | RETURNED | REMARK | FAILURE | SL | DATE | MOTOR | WORK | REMARK
1 | 132kW | KBL | 3990806/1 | Conv. 1.1 | 2017-01-06 |  |  |  | 1 |  | 132 KW-HT-KBL | Rewinding
2 | 150kW | CG | 2003211/4 | Conv.2.1 | 2017-04-24 | [5 empty] | SL:3990806-1
3 | 200kW | CG | 2003210/3 | Conv. C7 | 2017-08-15 | 2019-04-08 | Returned unrepaired
4 | 200kW | CG | 2003210/4 | Conv. C2 | 2018-05-15 | 2020-04-24 | Failed within 10 Hrs of running |  | 2 | 24.04.2017 | 150kW-HT-CG | Rewinding
5 | 480kW | CG | 2002043/1 | GC-3 | 2019-12-05 |  |  | 03.12.2019, |  |  | SL: 2003211/4
6 | 250kW | KBL | 3080909/3 | Conv. C-8P | 2019-08-19 |  |  | 09.08.2019,
7 | 200kW | CG | 2003210/5 | Conv. 2.1 | 2020-02-05 |  |  | 22.09.2019, | 3 | 15.08.2017 | 200kW-HT- | Rewinding
8 | 150kW | CG | 2003211/2 | Conv. C2 | 2020-02-05 |  |  | 19.02.2019, |  |  | SL:2003210/3
[9 empty] | 4 | 15.05.2018 | 200kW-HT-CG | Rewinding
SL: NA
[9 empty] | 06.01.2017 | 05.02.2020 | 200kW-HT-CG | Rewinding | Conv 2.1, failed on 22.09.2019
SL:2003210/5
[9 empty] | 6 | 05.02.2020 | 150kW-HT-CG | Rewinding | Conv C2, failed on
[11 empty] | SL:2003211/2 |  | 19.02.2019
[9 empty] | 7 | 05.12.2019 | 480kW-HT-SLIM-CG | Motor earth and bearing failure | GC-3, failed on 03.12.2019
SL:2002043/01

## Failed
DETAILES OF FAILED HT MOTORS
SL | KW | MAKE | USE AT / LOCATION | SL NO | FAILURE DATE
1 | 125 | Kirloskar | Conveyor 1.1 Primary drive | 3000807-1 | 19.07.2019
2 | 150 | Hyundai | Conveyor 2.2 drive | 89MSTH015 | 12.08.2019
3 | 150 | Crompton Greaves | Conveyor C7 A Primary | 2003211/3 | 408735
4 | 150 | Crompton Greaves | Conveyor C2 A Secondary | 2003211/2 | 2019-02-19
5 | 200 | Crompton Greaves | Conveyor C5 A | 2003210/3 | 2019-03-17
6 | 200 | Crompton Greaves | Conv 2.1 | 2003210/5 | 21.10.2019

## CWS-update
CHP motors at CWS
SL | RATING (kW) | MAKE | SL | USE | SENT | RETURNED | REMARK
1 | 132 | KBL | 3990806/1 | Conv. 1.1 | 2017-01-06
2 | 150 | CG | 2003211/4 | Conv.2.1 | 2017-04-24
3 | 150 | CG | 2003211/2 | Conv. C2 | 2020-02-05
4 | 200 | CG | 2003210/4 | Conv. C2 | 2020-07-11
5 | 200 | CG | 2003210/5 | Conv. 2.1 | 2020-02-05
6 | 250 | KBL | 3080909/3 | Conv. C-8P | 2019-08-19
7 | 480 | CG | 2002043/1 | GC-3 | 2019-12-05

## Motor data
Status of Drive motors of CHP
SL | CAPACITY (kW) | INSTALLED | DEPLOYMENT | SPARE | BD | REMARK
1 | 480 kW | 1 | Gyratory Crusher 3 : 1 no | 0 | 1 | 1 BD motor is under reapair at CWS
2 | 400 kW | 2 | Gyratory Crusher 1 and 2 : 2 nos | 1 | 0 | 1 spare motor repaired at CWS is available at CHP.
3 | 355 kW | 2 | Conv C10, C11 | 1 | 0 | One spare motor is at DCH regional store.
4 | 250 kW | 7 | Conv 5.1P, 5.1S, 5.2P, 5.2S, C2P, C8P, C8S : 7 nos | 2 | 1 | 1 no BD motor is under repair at CWS. 2 nos avilable spare motors are only compatible with conv 5.1 and 5.2 due to frame height difference.
5 | 225 kW | 1 | Conv 2.2 : 1 no | 0 | 0 | 225 is generally not used in CHP. One 225kW motor obtained from E&M-Mines is fitted in conv 2.2 as the original capacity of 150kW was not available.
6 | 200 kW | 3 | Conv C2S, C5 , C7S : 3 nos | 1 | 2 | 1 nos under repair at CWS, 1 no at CHP for which rewinding estimated has been processed. It is at tendering stage. 1 no spare motor is available at CHP.
7 | 150 kW | 3 | Conv-2.1, C3, C7P : 3 nos | 0 | 4 | 2 nos BD motors under repair at CWS, 1 no is under repair with M/s M N Enterp. 1 no is at CHP.
8 | 132 kW | 4 | Conv- 1.1 : 2 nos conv 1.2 : 2 nos | 0 | 1 | 1 no motor under repair at CWS
9 | 125 kW | 0 |  | 0 | 1 | 125kW motor was originally installed in pump house, it can be fitted in conv 1.1 and 1.2. 1 BD motor is under repainring with M/s M N Ent.
10 | 110 kW | 1 | Conv-C9: 1 no | 1 | 0 | Spare 1 no is only comatible with ETP pump which is presently running with 90kW motor.
11 | 90 kW | 10 | PF 1,2, 3, 4 : 4 nos Conv 3.1, 3.2, 4.1, 4.2, C4: 5 nos ETP Pump : 1 no | 2 | 4 | Spare: 1 no compatible with conv another compatible for plough. 4 nos under repair with M/s National Enterp. 1 no repaired by M/s National electrical is faulty.
12 | 75 kW | 2 | PF 5, 6 : 2 nos | 0 | 1 | 1 no under repair with M/s National Enterp.
13 | 55 kW | 6 | Silo : 4 nos AF-1, AF-3: 2 nos | 1 | 0 | A new spare motor is available.
14 | 37 kW | 5 | DE system : 3 nos conv C1: 1 no AF-2: 1 no | 2 | 0 | 1 spare motor has welded base, which can only be fitted in DE system.

## Motor MB
CHP MOTORS MB
SL | MOTOR TYPE | QUANTITY
1 | 37 kW, 1480 rpm, 3 Phase, LT motor, frame: | 1
2 | 37 kW, 1480 rpm, 3 Phase, LT motor, frame:255 | 2
3 | 55 kW, 1480 rpm, 3 Phase, LT motor, frame:250 | 1
4 | 75 kW, 1480 rpm, 3 Phase, LT motor, frame:280 | 2
5 | 90 kW, 1480 rpm, 3 Phase, LT motor, frame:280 | 4
6 | 90 kW, 1447 rpm, 3 Phase, LT motor, frame:315 | 5
7 | 110 kW, 1480 rpm, 3 Phase, HT motor, frame:315 | 1
8 | 132 kW, 1480 rpm, 3 Phase, HT motor, frame:400 | 4
9 | 150 kW, 1480 rpm, 3 Phase, HT motor, frame:355 | 2
10 | 150 kW, 1480 rpm, 3 Phase, HT motor, frame:425 | 2
11 | 200 kW, 1480 rpm, 3 Phase, HT motor, frame:355 | 5
12 | 250 kW, 1480 rpm, 3 Phase, HT motor, frame:355 | 2
13 | 250 kW, 1500 rpm, 3 Phase, HT motor, frame:475 | 4
14 | 355 kW, 1480 rpm, 3 Phase, HT motor, frame:400 | 2
15 | 400 kW, 992 rpm, 3 Phase, HT motor, frame: | 2
16 | 480 kW, 593 rpm, 3 Phase, HT motor, frame:560 | 1
TOTAL |  | 40

## CONVEYOR DETAILS (hidden)
SL | LOCATION | BELT LENGTH-M | WIDTH-MM | TYPE | PULL CHORD | BELT SWAY | ZERO SPEED | REMARK | LOCATION_CODE
1 | CONV 1.1-P
2 | CONV 1.1-S
3 | CONV 1.2-P
4 | CONV 1.2-S
5 | CONV 2.1
6 | CONV 2.2
7 | CONV 3.1
8 | CONV 3.2
9 | CONV 4.1
10 | CONV 4.2
11 | CONV 5.1-P
12 | CONV 5.1-S
13 | CONV 5.2-P
14 | CONV 5.2-S
15 | CONV C1 | 42 | 1400 | NN | 2 SIDE | Y | NF
16 | CONV C2-P | 470 | 1400 | SC | 2 SIDE | Y | NF
17 | CONV C3 | 207 | 1400 | NN | 1 SIDE | Y | NF
18 | CONV C4 | 398 | 1400 | NN | 1 SIDE | Y | NF
19 | CONV C5
20 | CONV C6
21 | CONV C7-P
22 | CONV C7-S
23 | CONV C8-P
24 | CONV C8-S
25 | CONV C9
26 | CONV C10
27 | CONV C11

## Sheet2 (hidden)
LOCATION | CODE | CONTROL SS
PHASE 1 CRUSHER HOUSE | 1 | 1
CONV 1.1-1.2 | 2 | 1
CONV 2.1-2.2 | 3 | 1
CONV 3.1-3.2 | 4 | 1
CONV 4.1-4.2 | 5 | 2
CONV 5.1-5.2 | 6 | 2
SILO-1 | 7 | 2
PHASE 2 CRUSHER HOUSE | 8 | 4
CONV C1 | 9 | 4
CONV C2 | 10 | 4
CONV C3 | 11 | 4
CONV C4 | 12 | 4
CONV C5 | 13 | 5
CONV C6 | 14 | 4
CONV C7 | 15 | 5
CONV C8 | 16 | 5
CONV C9 | 17 | 5
CONV C10 | 18 | 5
CONV C11 | 19 | 5