## Estimate
RECASTED ESTIMATE
Repairing, rewinding of 2 nos, LT induction motors 15kW and 22kW used in CHP, Dudhichua Project.
SL | DESCRIPTION | QTY | UNIT | RATE (Rs) | AMOUNT (Rs)
1 | Supply of Super enamel new copper wire. And Buyback of same amount of scrap copper. | 37 | kg | 325 | 12025
2 | Supply of Normex paper. | 0.6 | kg | 2000 | 1200
3 | Supply of Varnish | 4 | ltrs | 415 | 1660
4 | Supply of insulating items | 2 | set | 1670 | 3340
5 | Labour cost including contractor profit | 2 | job | 3924.8 | 7849.6
TOTAL |  |  |  |  | 26075
GST @ 18% |  |  |  |  | 4694
TOTAL WITH GST |  |  |  |  | 30769
Incharge/CHP Dy.Mgr(E&M)/CHP SOE(E&M)/CHP Foreman/CHP

## Labour Analysis
LABOUR COST ANALYSIS
Repairing, rewinding of 2 nos, LT induction motors 15kW and 22kW used in CHP, Dudhichua Project.
Works: | For each motor following works are required.
| 1 | Dismantling work.
| 2 | Taking out of burnt coils.
| 3 | Making coil of new copper wire.
| 4 | Fixing of new coils in place.
| 5 | Fitting of terminal bushes.
| 6 | Reassembly work.
| 7 | Heating.
| 8 | Testing.
Cost : | Above defined volume of work for each motor can be carried out
| by a gang of 2 skilled and 2 unskilled labors in |  |  |  | 2 | shifts.
|  | TYPE | MANSHIFTS | RATE | AMOUNT
|  | SKILLED | 4 | 522 | 2088
|  | UN SKILLED | 4 | 370 | 1480
|  | LABOUR COST |  |  | 3568
|  | CONTRACTOR PROFIT @ 10% |  |  | 356.8
|  | TOTAL |  |  | 3924.8
Incharge/CHP Dy.Mgr(E&M)/CHP SOE(E&M)/CHP Foreman/CHP

## Material Analysis
MATERIAL ANALYSIS
Repairing, rewinding of 2 nos, LT induction motors 15kW and 22kW used in CHP, Dudhichua Project.
SL | ITEM | QUANTITY ESTIMATION |  |  | RATE JUSTIFICATION
|  | Basis | Qty | Unit | Basis | Rete per Unit (in Rs.)
1 | Supply of Super enamel new copper wire. And Buyback of same amount of scrap copper. | Approximated as 1kg copper per kW rating. 15kg + 22kg = 37kg | 37 | kg | Rate as per wo no : DCH/SO(E&M)/WO/CHP/18-19/38 DTD 19.06.2018 | 325
2 | Supply of Normex paper. | 2 x (0.3 kg per machine) | 0.6 | kg | Rate as per wo no : DCH/SO(E&M)/WO/CHP/18-19/38 DTD 19.06.2018 | 2000
3 | Supply of Varnish | 2 x (2 Ltrs per machine) | 4 | ltrs | Rate as per wo no : DCH/SO(E&M)/WO/CHP/18-19/38 DTD 19.06.2018 | 415
4 | Supply of insulating items | 2 x (1 set per machine) | 2 | set | Rate as per wo no : DCH/SO(E&M)/WO/CHP/18-19/38 DTD 19.06.2018 | 1670
Incharge/CHP Dy.Mgr(E&M)/CHP SOE(E&M)/CHP Foreman/CHP

## Motors
DETAILES OF FAILED LT MOTORS
SL | KW | MAKE | USE | SL NO
1 | 15 | Siemens | Sump pump | 154679
2 | 22 | Siemens | ventilation fan | 154780
|  | I/c CHP-DCH | Dy Mgr(E&M)/CHP | SOE(E&M)/CHP