## Estimate
RECASTED ESTIMATE
Repairing, rewinding of LT induction motors 1 nos 22kW, 2 nos 7.5kW and 2 nos 5.5kW kW used in CHP, Dudhichua Project.
SL | DESCRIPTION | QTY | UNIT | RATE (Rs) | AMOUNT (Rs)
1 | Supply of Super enamel new copper wire. And Buyback of same amount of scrap copper. | 48 | kg | 325 | 15600
2 | Supply of Normex paper. | 1.5 | kg | 2000 | 3000
3 | Supply of Varnish | 7.5 | ltrs | 415 | 3112.5
4 | Supply of insulating items | 4 | set | 1670 | 6680
5 | Labour cost including contractor profit | 1 | job | 12100 | 12100
TOTAL |  |  |  |  | 40493
GST @ 18% |  |  |  |  | 7289
TOTAL WITH GST |  |  |  |  | 47782
Incharge/CHP Dy.Mgr(E&M)/CHP SOE(E&M)/CHP Foreman/CHP

## Labour Analysis
LABOUR COST ANALYSIS
Repairing, rewinding of LT induction motors 1 nos 22kW, 2 nos 7.5kW and 2 nos 5.5kW kW used in CHP, Dudhichua Project.
Works: | For each motor following works are required.
| 1 | Dismantling work.
| 2 | Taking out of burnt coils.
| 3 | Making coil of new copper wire.
| 4 | Fixing of new coils in place.
| 5 | Fitting of terminal bushes.
| 6 | Reassembly work.
| 7 | Heating.
| 8 | Testing.
Cost : | The defined work for all five motor can be carried out
| by a gang of 1 skilled and 2 unskilled labors in |  |  |  | 8 | shifts.
|  | TYPE | MANSHIFTS | RATE | AMOUNT
|  | SKILLED | 8 | 569 | 4552
|  | UN SKILLED | 16 | 403 | 6448
|  | LABOUR COST |  |  | 11000
|  | CONTRACTOR PROFIT @ 10% |  |  | 1100
|  | TOTAL |  |  | 12100
Incharge/CHP Dy.Mgr(E&M)/CHP SOE(E&M)/CHP Foreman/CHP

## Material Analysis
MATERIAL ANALYSIS
Repairing, rewinding of LT induction motors 1 nos 22kW, 2 nos 7.5kW and 2 nos 5.5kW kW used in CHP, Dudhichua Project.
SL | ITEM | QUANTITY ESTIMATION |  |  | RATE JUSTIFICATION
|  | Basis | Qty | Unit | Basis | Rete per Unit (in Rs.)
1 | Supply of Super enamel new copper wire. And Buyback of same amount of scrap copper. | Approximated as 1kg copper per kW rating. 1 x 22kg + 2 x 7.5kg + 2 x 5.5kg + = 48kg | 48 | kg | Rate as per wo no : DCH/SO(E&M)/WO/CHP/18-19/38 DTD 19.06.2018 | 325
2 | Supply of Normex paper. | 5 x (0.3 kg per machine avg) | 1.5 | kg | Rate as per wo no : DCH/SO(E&M)/WO/CHP/18-19/38 DTD 19.06.2018 | 2000
3 | Supply of Varnish | 5 x (1.5 Ltrs per machine avg) | 7.5 | ltrs | Rate as per wo no : DCH/SO(E&M)/WO/CHP/18-19/38 DTD 19.06.2018 | 415
4 | Supply of insulating items | 5 x (1 set per machine) | 4 | set | Rate as per wo no : DCH/SO(E&M)/WO/CHP/18-19/38 DTD 19.06.2018 | 1670
Incharge/CHP Dy.Mgr(E&M)/CHP SOE(E&M)/CHP Foreman/CHP

## Motors
DETAILES OF FAILED LT MOTORS
SL | KW | MAKE | USE | SL NO | INSTALLATION YEAR | FAILURE DATE | EXPENDITURE IN LAST THREE YEARS
1 | 22 | Siemens | Ventilation | N8/154779 | 1993 | 2020-01-01 | Not repaired in last three years
2 | 7.5 | CG | Lubrication pump | NA | 2005 | 2020-03-01 | Motor once repaird in 2017 for approx Rs.7000.
3 | 7.5 | CG | Lubrication pump | NA | 2005 | 2020-02-01 | Not repaired in last three years
4 | 5.5 | ABB | Exhaust | 73993 | 2005 | 2019-11-01 | Not repaired in last three years
5 | 5.5 | ABB | Exhaust | 74694 | 2005 | 2020-02-01 | Not repaired in last three years
|  | I/c CHP-DCH |  | Dy Mgr(E&M)/CHP |  | SOE(E&M)/CHP